## Joint Types
Joint # | Joint Type | Applicable Systems | Connection Method | Hardware Required | Key Dimensions | Construction Steps | Data Centre Application | 3D Model Notes | Ezystrut Part Codes
1 | Straight Splice | ET3, ET5, NEMA, CT | Splice plates on OUTSIDE of both side rails, bridging the gap between two tray ends. | 2x splice plates (one per side) SBH smooth-head bolts CNH cage nuts 4 bolts per side minimum | Splice overlap: 75mm each side of joint Gap between tray ends: 3-5mm Splice plate height: 80% of rail height | 1. Butt two tray sections end-to-end (3-5mm gap) 2. Place splice plate centred on joint, outside of side rail 3. Insert SBH bolts through pre-punched holes (smooth head INSIDE) 4. Secure with CNH cage nuts 5. Repeat on other side 6. Check electrical continuity (star washer if pre-galv) | Every straight run >3m (ET) or >6m (NEMA) requires splices. In data centres: along corridors, within data halls, between switchrooms. | Model as: Tray_1 ¦ 5mm gap ¦ Tray_2 Splice plates visible as yellow rectangles on outside of rails. Smooth bolt heads NOT visible from inside. | ET5S (ET5 splice) ET3S (ET3 splice) SBH + CNH fasteners
2 | Horizontal 90° Bend (Factory Fitting) | NEMA, CT | Separate pre-made bend FITTING connects to straights via splice plates (NEMA) or taper-fit (CT). The bend is its own piece - NOT part of the straight tray. | NEMA: 1x bend fitting + 4x splice plates (2 per end) CT: 1x CTB fitting + M6x10 WIZZ screws + M6 flanged nuts | Radius: 300mm (NEMA1) or 450mm (NEMA2/3/4) CT: Fixed 150mm radius (all CT fittings) Angle: 90° standard Custom: 600, 900mm radius available | NEMA: 1. Position bend fitting between two straight sections 2. Splice plate on each rail at each end (4 total) 3. Bolt through with SBH/CNH CT: 1. Slide tapered end of CTB into straight CT 2. Align base perforations 3. Fix with M6x10 WIZZ screws through base holes | Direction changes in cable routes. In data centres: turning corners in corridors, routing around columns, entering/exiting rooms at 90°. | THREE separate pieces in the model: Straight_1 → [splice] → Bend_Fitting → [splice] → Straight_2 Bend fitting has CURVED rungs (NEMA) or curved perforated base (CT). Never model as a single piece bending. | NEMA3 bend (by width+radius) CTB (CT bend) WIZZ fasteners (CT)
3 | Horizontal Bend (ET Field-Fabricated) | ET3, ET5 | Tray is CUT at the bend point and the BASE is bent in-situ. A Radius Plate (RP) supports the curve from UNDERNEATH. Cut side rails are re-closed with splice plates. | 1x Radius Plate (RP) - 2m length, cut to suit 2-4x splice plates for rail cuts SBH + CNH fasteners | Radius: Adjustable (set by RP position) Typical: 300-600mm RP sits flush under tray base Cut in rail: ~50-100mm opening per side | 1. Mark bend location using RP as template 2. Cut BOTH side rails at bend point (tin snips or grinder) 3. Position RP underneath tray base, curved to desired radius 4. Bend tray base over the RP to desired angle 5. Bolt RP to tray base through pre-punched holes 6. Close rail cuts with splice plates on outside 7. Secure all with SBH/CNH | Any angle bend in ET systems. Preferred for non-90° angles and adjustable radii. In data centres: routing around services, angled entries to switchboards, custom angles for site geometry. | CONTINUOUS tray base (no gap at bend). RP visible as green plate UNDER the base at the curve. Splice plates visible as yellow on the rail cuts. Rail has visible cut lines at start/end of curve. | ET5RP (radius plate) ET3RP (radius plate) ET5S / ET3S (splices for cuts)
4 | Tee Junction (T-intersection) | ET3, ET5, NEMA, CT | ET: Main tray rail is CUT to create opening. Branch tray enters the cut. TX bracket bolts across joint on both sides. NEMA/CT: Pre-made tee fitting with 3 splice/taper connections. | ET: 2x TX brackets + splice bolts NEMA: 1x tee fitting + 6x splice plates CT: 1x CTT fitting + WIZZ screws | Branch width: same or narrower than main Radius at branch entry: 150mm (CT) or 300-450mm (NEMA) ET: Opening in main rail = branch width + 10mm | ET: 1. Mark branch entry point on main tray rail 2. Cut side rail at mark (branch-width opening) 3. Bend cut flap DOWN (out of cable path) 4. Insert branch tray into opening 5. Bolt TX bracket across joint (both sides) CT/NEMA: 1. Position tee fitting at junction point 2. Connect all 3 arms via splice/taper | Splitting cable routes. In data centres: main corridor feeds branching into each row, PDU feeds branching from sub-mains, BMS tray splitting to zones. | Main tray is CONTINUOUS (base unbroken). Branch enters through CUT in main rail. TX brackets (blue) visible on both sides of the cut. Branch tray base aligns with main tray base (flush). | ET5TX (tee/cross bracket) ET3TX CTT (CT tee fitting)
5 | Cross Junction (4-way intersection) | ET3, ET5, NEMA, CT | Same as Tee but BOTH rails of main tray are cut. Two branches enter from opposite sides. TX brackets on all 4 cut points. | ET: 4x TX brackets + splice bolts NEMA: 1x cross fitting + 8x splice plates CT: 1x CTC fitting + WIZZ screws | All 4 arms same width (standard) Radius at each entry: per system standard Centre area: open (cables cross freely) | ET: 1. Cut BOTH side rails at cross point 2. Bend flaps down on all 4 cuts 3. Insert branch trays from both sides 4. TX bracket on each of the 4 cut points CT/NEMA: 1. Position cross fitting 2. Connect all 4 arms via splice/taper | Major distribution intersections. In data centres: where main N-S and E-W cable routes cross, central distribution points, above MSB areas. | 4 tray arms meeting at centre. TX brackets (blue) at all 4 rail cuts. Centre area is OPEN (no rungs/base obstructing cable crossover). All 4 arms at same height (flush). | ET5TX (×4) ET3TX (×4) CTC (CT cross fitting)
6 | External Riser (Vertical UP - cable on outside) | ET3, ET5, NEMA, CT | Horizontal tray transitions to vertical. Riser Link (RL) brackets connect the two planes. Cable sits on OUTSIDE of the bend curve (tension side). | ET: 2x Riser Links (one per side) + bolts NEMA: 1x external riser fitting + splice plates CT: 1x CTER fitting + WIZZ screws | Radius: 300-600mm (must suit largest cable) Vertical section height: as required RL bracket length: varies with angle Support within 300mm of direction change (AS/NZS 3000) | ET: 1. Cut tray at transition point 2. Form vertical section (separate tray piece) 3. Bolt RL bracket on each side, bridging horizontal to vertical 4. Ensure minimum radius suits cable CT/NEMA: 1. Splice/taper external riser fitting between horizontal and vertical straights | Cable riser going UP from a lower level. In data centres: from basement to ground floor, from under-floor to overhead tray, from transformer pit up to cable corridor. | Two tray planes at 90° (horizontal + vertical). RL bracket (orange) visible on each side at the corner. Cable path is on the OUTSIDE of the curve. Support bracket modelled within 300mm of bend. | ET5RL (riser link) ET3RL CTER (CT external riser)
7 | Internal Riser (Vertical DOWN - cable on inside) | ET3, ET5, NEMA, CT | Horizontal tray transitions to vertical going DOWN. Cable sits on INSIDE of bend curve (compression side). Same hardware as external riser but inverted geometry. | ET: 2x Riser Links (one per side) + bolts NEMA: 1x internal riser fitting + splice plates CT: 1x CTIR fitting + WIZZ screws | Same as external riser. Cable bend radius is SMALLER than external (cable on inside = tighter bend for same fitting radius). Must verify cable bend radius is still met. | Same as external riser but: - Cables experience compression not tension - Gravity assists cable in staying in tray - Hold-down clips recommended on vertical section | Cable drop from overhead tray to equipment. In data centres: overhead tray dropping down to switchboard, tray dropping into under-floor space, drops to rack-mounted PDUs. | Two tray planes at 90° (horizontal → vertical down). RL bracket (orange) on each side. Cable path on INSIDE of curve. Hold-down clips on vertical section. | ET5RL (riser link) ET3RL CTIR (CT internal riser)
8 | CT Taper-Fit (Telescope Connection) | CT only | CT tray and all CT fittings have TAPERED fold edges. One end tapers inward, the other outward. They telescope together (slide-fit) and are screwed through the base perforations. | M6 x 10 screws + M6 flanged nuts Ordering code: WIZZ Minimum 2 screws per joint | Overlap: 30-50mm Taper angle: ~5° fold on side wall edges Side wall: 20mm height (low profile) Base: continuously perforated (screw anywhere) | 1. Identify tapered-IN end and tapered-OUT end 2. Slide OUT taper of one piece INTO the IN taper of the next 3. Overlap ~30-50mm until edges are flush 4. Align base holes 5. Insert M6x10 screw from below 6. Secure with M6 flanged nut on top 7. Minimum 2 fixings per joint | ALL CT system connections. CT is light-duty only. In data centres: data/comms cable trays, fibre trays, BMS/control cable trays, security cable routes. NOT for heavy power cables. | Overlap zone visible as slightly thicker area where two pieces telescope. No separate splice plate - the tray edges ARE the connection. Low profile (20mm sides) - distinct from ET/NEMA. Perforated base pattern visible. | CT (straight) CTB (bend) CTT (tee) CTC (cross) CTER / CTIR (risers) WIZZ fasteners
9 | Straight Reducer (Width Transition) | NEMA, ET (field-cut) | Tapered fitting transitions between two different tray widths. Connects via splices at each end. One end matches width W1, other matches width W2. | NEMA: 1x reducer fitting + 4x splice plates ET: Field-cut taper in tray + splice plates Alternatively: left-hand or right-hand reducer (asymmetric) | W1 (wide end): e.g. 600mm W2 (narrow end): e.g. 300mm Length: typically 600mm transition Angle: determined by (W1-W2)/2 ÷ length | NEMA: 1. Splice wide tray to wide end of reducer 2. Splice narrow tray to narrow end of reducer ET field-cut: 1. Cut tray sides at angle from W1 to W2 2. Bend side walls to follow new width 3. Splice plates at transition points | Where cable count reduces (fewer cables = narrower tray). In data centres: main corridor (900mm) reducing at each branch after cables peel off, approaching a switchboard where only a few cables remain. | Trapezoidal shape in plan view. Wide end flush with wide tray. Narrow end flush with narrow tray. Splice plates at both ends. Base is continuous (single piece). | NEMA reducer (by W1 x W2) Left/Right hand variants ET5S splices at cuts
10 | Offset / S-Bend (Lateral Shift) | ET3, ET5, NEMA | Two opposing bends (one left, one right) connected by a short straight, shifting the tray laterally. Uses 2x radius plates (ET) or 2x bend fittings + 3x splice sets (NEMA). | ET: 2x RP + 4x splice plates NEMA: 2x bend fittings + 6x splice plates | Lateral offset: typically 200-600mm Angle: usually 30° or 45° each bend Straight between bends: min 300mm Total length: offset/sin(angle) + 2×radius×tan(angle/2) | 1. First bend (angle away from centreline) 2. Short straight at the offset angle 3. Second bend (angle back to original direction) Result: tray exits parallel to entry but shifted laterally. | Avoiding obstructions. In data centres: routing around columns, dodging ductwork, shifting tray alignment between rooms, accommodating structural beams. | Three-section assembly: Bend_1 + Angled_Straight + Bend_2. RP (green) visible under each bend. Entry and exit straights are PARALLEL but offset. All sections at same height (horizontal offset only). | 2x ET5RP (radius plates) 4x ET5S (splices) Or 2x NEMA bend fittings

## Connection Rules
CONNECTION RULES MATRIX
What can connect to what, and what goes between them
From Component | To Component | Connection Piece | System | Rule
Straight | Straight | Splice plate (S) | All | ALWAYS required. Cannot butt tray ends directly. Splice bridges the gap on OUTSIDE of rails.
Straight | 90° Bend | Splice plate (S) | NEMA | Bend is separate fitting. Splice on each rail at each end of bend.
Straight | 90° Bend | Radius Plate (RP) | ET3/ET5 | NO separate bend piece. Cut tray rails, bend base in-situ, RP underneath.
Straight | 90° Bend | Taper slide-fit | CT | CTB bend telescopes into CT straight. WIZZ screws through base.
Straight | Tee branch | TX Bracket | ET3/ET5 | Cut main rail. Branch enters cut. TX brackets bridge joint on both sides.
Straight | Tee branch | Splice plate (S) | NEMA | Pre-made tee fitting. Splice all 3 arms.
Straight | Tee branch | Taper slide-fit | CT | CTT tee telescopes into straights on all 3 arms.
Straight | Vertical (up) | Riser Link (RL) | ET3/ET5 | Cut tray at transition. RL bracket on each side bridges horizontal to vertical.
Straight | Vertical (up) | Splice plate (S) | NEMA | Pre-made external riser fitting. Splice both ends.
Straight | Vertical (up) | Taper slide-fit | CT | CTER fitting telescopes into horizontal and vertical straights.
Straight | Vertical (down) | Riser Link (RL) | ET3/ET5 | Same as up but inverted. Add hold-down clips on vertical section.
Straight | Vertical (down) | Taper slide-fit | CT | CTIR fitting telescopes into horizontal and vertical straights.
Straight | Reducer | Splice plate (S) | NEMA/ET | Splice at wide end AND narrow end. Reducer is separate transition piece.
Bend | Bend | Short straight + 2x splice | NEMA | For S-bends: two bends connected by minimum 300mm straight with splices.
Bend | Bend | 2x RP (one per bend) | ET3/ET5 | For S-bends: two field-cuts with RPs. Short straight between.
Vertical | Vertical | Splice plate (S) | All | Same as horizontal straight-to-straight. Splice on outside of rails.
Straight | Equipment | End plate / gland plate | All | Tray terminates at switchboard/panel. End plate closes the tray. Earth bond to equipment.
Straight | Wall | Fire collar / penetration | All | Through fire-rated walls: fire-rated cable tray penetration seal required per AS/NZS 3013.

## Prohibited Connections
PROHIBITED CONNECTIONS
These configurations are physically impossible or non-compliant
Prohibited Action | Why It Fails | Correct Alternative
Butt two tray ends together (no splice) | No structural connection. Joint will separate under cable weight. No earth continuity. Fails AS/NZS 3000. | Use splice plates (S) on outside of both rails, bolted through with SBH/CNH.
Directly merge bend into straight (shared edge) | Raised side rails of both pieces interfere. No physical way to mate two upstanding flanges edge-to-edge. | ET: Cut rails and use RP underneath (continuous base). NEMA/CT: Separate bend fitting with splice/taper between.
CT bend with radius other than 150mm | ALL CT fittings are manufactured at fixed 150mm radius. Cannot be field-modified. | If larger radius needed: use ET3/ET5 system with RP (adjustable radius) or NEMA with custom-order bend.
Mix CT fittings with ET3/ET5 tray | Different profiles, different side heights (20mm vs 50/85mm), different connection methods. Incompatible. | Use only one system per run. Transition between systems requires an end plate on each + new support.
Mix NEMA ladder with ET cable tray | Different rail profiles, different rung/base construction, different splice hardware. Incompatible. | Use only one system per run. Plan system boundaries at logical transition points (room entries, risers).
Bend tighter than cable minimum radius | Cable insulation damage, reduced current capacity, potential fault. CT 150mm radius only suits cables ≤25mm². | Select fitting radius ≥ largest cable's minimum installed bend radius. Upsize to 300/450/600mm radius as needed.
Unsupported joint (no bracket within 300mm) | Joint under load will sag/fail. Non-compliant with AS/NZS 3000 cl. 3.9.5. | Install support bracket within 300mm of EVERY direction change, junction, and termination point.
Vertical run without hold-down clips | Cables slide down under gravity, bunch at bottom, overload bottom support. | Hold-down clips (HD) at maximum 1.5m intervals on ALL vertical sections. Minimum 2 per vertical run.
Tee branch wider than main tray | Branch cannot physically fit through cut in main rail. Structural weakness. | Branch must be same width or narrower than main. Use reducer if branch needs to be wider downstream.
Cover across a joint without cover splice | Cover ends will gap/separate at joint, defeating protection purpose. | Use matching cover fittings: cover bend, cover tee, cover splice. Each tray fitting has a matching cover fitting.

## Part Numbers
EZYSTRUT PART NUMBER DECODER
Format: [System][Width][Finish]
Accessories: [System][Accessory][Finish]
System Prefix |  | Finish Suffix
ET | EzyTray (light) | G | Pre-Galvanised
ET3 | ET3 Cable Tray (medium) | H | Hot Dip Galvanised
ET5 | ET5 Cable Tray (heavy) | S | Stainless Steel
CT | CT Perforated Tray | A | Aluminium (ET3 only)
CTB | CT Bend
CTT | CT Tee | Accessory Codes
CTC | CT Cross | S | Splice
CTIR | CT Internal Riser | TX | Tee/Cross Bracket
CTER | CT External Riser | RL | Riser Link
|  | HD | Hold Down Unit
Widths (mm) |  | RP | Radius Plate
75 |  | DS | Divider Strip
100 |  | SHB | Side Hanger Bracket
150
225 |  | Example Part Numbers
300 |  | ET5600G | ET5 tray, 600mm wide, pre-galvanised
450 |  | ET5SG | ET5 splice, pre-galvanised
600 |  | ET5RPG | ET5 radius plate, pre-galvanised
900 |  | ET5TXH | ET5 tee/cross bracket, hot-dip galv
|  | ET5RLG | ET5 riser link, pre-galvanised
|  | CT300G | CT tray, 300mm wide, pre-galvanised
|  | CTB300G | CT bend, 300mm wide, pre-galvanised
|  | CTT150G | CT tee, 150mm wide, pre-galvanised